## Sheet1
Load management forecast tool
| Transport asset and operation definition |  |  |  |  | Checks and balances
1 | No. Evs | 5 |  | User defined | Fleet size at the site | Battery capacity meets daily needs | TRUE
2 | Simultaneous charging (%) | 100% |  | User defined | Diversity/ concurrency assumption | Charger power sufficient for dwell | TRUE
3 | Avg. daily distance (km) | 200 |  | User defined | per truck | Overnight charging feasible | TRUE
4 | EV Consumption (kwh/km) | 1.4 |  | User defined | per truck | Energy consumption in expected range | TRUE
5 | Battery size (kwh) | 400 |  | User defined | OEM spec | Rated hardware + Simultaneity feasible? | TRUE
6 | Average daily Depth of Discharge (%) | 80% |  | User defined | Usable share of battery
7 | Usable battery capacity (kwh) | 320 | D9*D10 | Calculated | Check only (don't plan to exceed)
8 | Rated charger power (kW) | 150 |  | User defined | Chosen charger size
9 | Connectors per charger | 2 |  | User defined | Number of plugs on one charger
10 | Max active ports/ charger | 2 |  | User defined | Number of ports that can deliver power simultaneously
11 | Per port power cap (kW) | 0 |  | User defined | If a port has its own max (else leave blank/0 to infer split)
12 | Charging window: Idle/dwell time (hrs) | 8 |  | User defined | Hours available to charge per day
13 | Energy per EV per day (kWh) | 280 | D7*D8 | Calculated | Daily energy that must be replenished.
Energy and Charger Requirements
14 | Concurrent Evs | 5 | CEILING(D5*D6,1) | Calculated | No. Evs charging simultaneously
15 | Effective per port power (kW) | 75 | IF(D15>0,MIN(D15, D12/D14),D12/D14) | Calculated | Power per port.
16 | Charger efficiency losses | 10% |  | Set | (grid -> battery, taper, conversion)
17 | Adjusted energy per EV (kWh) | 308 | D17*(1+D22) | Calculated | What the grid must deliver
18 | Time to charge at rated power (hrs) | 2.0533 | D23/D12 | Calculated
19 | Fleet minimum average power for energy: Pmin (Kw) | 192.5 | D5 * D23 / D16 | Calculated | adjusted energy demand/ dwell hours
20 | Chargers required (by energy) | 2 | CEILING(D25 / D12, 1) | Calculated | Satisfy total fleet energy within dwell
21 | Chargers required (by simultaneous charging) | 3 | CEILING(D20/D14, 1) | Calculated | Minimum based on concurrency
22 | Chargers required (final) | 3 | MAX(D27, D26) | Calculated
23 | Total active ports at peak | 5 | MIN(D20, D28*D14) | Calculated
24 | Peak with power-sharing | 375 | D29 * D21 | Calculated | Use for grid-capacity checks when you are sure power-sharing is enabled and enforced
25 | Fleet average EV load | 192.5 | MIN(D25, D28 * D12 ) | Calculated | Typical: Managed average (fits dwell)
26 | Fleet nameplate coincident peak (kW) | 450 | D28*D12 | Calculated | Worst case: Unmanaged peak (nameplate)
Facility capacity assumptions
27 | Contracted Grid connection (kW) | 500 |  | User defined | Use contracted limit not transformer kVA | Grid capacity adequate (managed) | TRUE
28 | Base load at facility (Kw) | 50 |  | User defined | Lighting, HVAC, MHE | Grid capacity adequate (peak with margin) | FALSE
29 | Total site load - average (kW) | 242.5 | D36+D31 | Calculated | With managed charging
30 | Grid utilisation - average (%) | 48.5% | D37/D35 | Calculated
31 | Headroom - average (kW) | 257.5 | D35-D37 | Calculated
32 | Grid safety margin (%) | 20% |  | Set | (fluctuations, brownouts, etc..)
33 | Total site load - peak (kW) | 500 | D36+D32 | Calculated | if chargers all pull nameplate
34 | Suggested connection for peak (kW) | 600 | D41*(1+D40) | Calculated | With safety margin
35 | Grid utilisation - peak (%) | 120% | D42/D35 | Calculated
36 | Headroom - peak (kW) | -100 | D35-D42 | Calculated